Wall-Mounted Temperature and Humidity Transmitter with Output R S485

(THM100-11M-YC)

The wall-mounted temperature and humidity transmitter with output RS485 adopts the imported high quality digital temperature sensor . It can reliably collect and distribute and control the signals with epistatic machine system.

Its major features are small size, light weight, wide measuring range, high precision, fast response and long-term stability, which makes it widely used in meteorology, national defense, scientific research, post and communications, chemical industry, environmental protection, medicine, hotel, food and logistic storages, HVAC and various kinds of areas which are needed to measure and control the temperature  and humidity of the air.

Technical data:

Operating voltage :        24VDC

Operating environment:    Humidity ≦95%RH, Temperature -20~+80℃

Input Signal:             SHT digital temperature and humidity sensor

Temperature Measuring range:   -40℃～+120℃

Humidity Measuring range:     0~100%RH

Output Signal:               RS-485 communication,Modbus RTU

Load Capacity:               ≦500ᴒ

RS-485 Wiring Diagram

(Note: It is important to ensure correct connection between A and B. Otherwise it can not normal communication between transmitter and computer. For long distance transmission , shielded twisted cable is recommended. )

24V: 24V DC power supply terminal ﹢;(power range :12V~24VDC)

5V:5V DC power supply terminal﹢;(According to the actual supply situation)

G:Power supply ground terminal(public terminal )

S:Sensor clock line terminals;( S+D temperature and humidity sensor )

D:Sensor data line terminals;( D , temperature sensor )

A:485Commucation A Terminal

B:485Commucation B Terminal

G：Shielded layer Terminal

Sw:Baud rate ,meter address setting DIP switch

J3:Terminal matching resistor jumper wire

1、2 short connect matching resistor 120 ᴒ

2、3 short connect matching resistor null(default)

LED1:meter working status indication

LED2:meter communication status indication

Sending and Receiving Data Command Format

Host sending terminal:

E.g. :01 03 00 00 00 02 CRCL CRCH

The first byte: device address

The second byte:function code (0×03)---(read holding registers)

The third byte:data starting address (0×00)---(high byte)

The fourth byte:data starting address(0×02)---(low byte)

The fifth byte:data number (0×00)---(high byte)

The sixth byte:data number (0×02)---(low byte)

The seventh byte:CRCL---16 bits CRC check low byte

The eighth byte:CRCH---16 bits CRC check high byte

Slave returning terminal :

E.g.:0×01 0×03 0×04 0×00 0×14 0×00 0×52  0x00 0x3F 0X00 0X05 CRCL CRCH

The first byte: device address

The second byte:function code (0×03)

The third byte:data byte number (0×08)---return to 8 data bytes

The fourth byte:temperature integer bit high byte(0×00)

The fifth byte:temperature integer bit low byte

The sixth byte:temperature decimal places high byte(0×00)

The seventh byte:temperature decimal places low byte

The eighth byte:humidity integer bit high byte(0×00)

The ninth byte:humidity integer bit low byte

The tenth byte:humidity decimal places high byte(0×00)

The eleventh byte:humidity decimal places low byte

The twelfth byte:CRCL--16 bits CRC check low byte

The thirteenth byte:CRCH---16 bits CRC check high byte

Temperature and humidity calculation method

- Determine the highest digits of temperature integer bits of low byte.when it equals to 0, it is positive temperature ; when it equals to 1, it means negative temperature. It starts to calculate after choosing the highest digits of temperature integer bits of low byte contrary.

- Temperature value =temperature integer bits after processing + temperature decimal places divided by 100

- Humidity value=humidity integer bits +humidity decimal places divided by 100

Physical Interface

- Information transmission :starting bit 1 bit, data bit 8bits, parity check ,stop bit 1 bit

- Baud rate range:1200 2400 4800 9600

- Device address range:1~32

- Factory default:baud rate 1200 address01

- Address, Baud rate setting: use the accessary serial debugging software, pick ModbusRTU,choose check CRC16(ModbusRTU),input and display HEX format.

- Change parameter command format:00 16+Baud rate+Device Address

- E.g: change Baud rate to 9600,device address is NO.32 ,debugging software

- Sending :00 16 96 20

- Returning:00 16 04 96 20 CRCL CRCH Error ! No found reference source

- Among:00 16 changing command

- 04   return to 4 bytes

- 20   device address setting NO.32

- 96   Baud rate 9600

- CRCL 16 bits CRC Check low byte

- CRCH 16 bits CRC Check high byte

- Note: It is necessary to know the current baud rate before changing.

- After changing, power on again. It works.